## Design
Using the design chart of CC/DV system based on the calculated peak sensible load per floor area ( 80-90 w/m2) and different values of P (flow rate parameter) below, we find the different parameters (chilled ceiling temperature (°C), supply air temperature (°C), load removal ratio, stratification height (m) and temperature gradient (°C/m)).
|  | room area |  |  | A | 25
|  | the peak total sensible load per floor area (W/m2) |  |  | Qs | 88
|  | chilled ceiling temperature (°C) |  |  | Tc | 16
|  | supply air temperature (°C) |  |  | Ts | 19
|  | load removal ratio |  |  | R | 0.5
|  | stratification height (m) |  |  | H | 1.578
|  | temperature gradient (°C/m) |  |  | dT/dZ | 1.4608
|  | peak sensible load (w/m2) |  |  | Qs | 88
|  | ratio of cooling load to supply mass flow rate P=Qs/m˙s ( kJ/kg) |  |  | P | 8
The following equations are used to assess if the proposed system satisfies thermal comfort and indoor air quality requirements.
|  | P | mdot | Tc | Ts | R | H | dT/dZ
|  | 4 | 0.55 | 17 | 18 | 0.3 | 1.7218 | 1.1621
|  | 6 | 0.36667 | 17 | 18 | 0.35 | 1.6456 | 1.2554
|  | 8 | 0.275 | 16 | 19 | 0.475 | 1.5801 | 1.4608
|  | 10 | 0.22 | 16 | 19 | 0.525 | 1.5039 | 1.5542
|  | 12 | 0.18333 | 15.5 | 20.5 | 0.575 | 1.4702 | 1.7035
|  | 14 | 0.15714 | 15.5 | 20.5 | 0.6 | 1.3961 | 1.8022
After satisfying the requirements of comfort ( H> 1m) and indoor air quality (dT/dZ<2.5 oC/m), the energy consumption of the DV and CC system can be found by doing the following:
a. Finding the exhaust air temperature Tr (°C) as follows:
Design | P | mdot | Ts | dT/dZ | Tr
1 | 4 | 0.55 | 18 | 1.1621 | 20.6147
2 | 6 | 0.36667 | 18 | 1.2554 | 20.8248
3 | 8 | 0.275 | 19 | 1.4608 | 22.2869
4 | 10 | 0.22 | 19 | 1.5542 | 22.4969
5 | 12 | 0.18333 | 20.5 | 1.7035 | 24.3329
6 | 14 | 0.15714 | 20.5 | 1.8022 | 24.5549
b- Finding the amount of reheat used from the following energy balance:
1000
Design | P | mdot | Tc | Ts | R | H | dT/dZ | Qcc | Qsdv | Qrh | Wv | Tdp,min | HR (wa, max) | Tdp | Ws. Max | m cond | Qc | fan power P (W) | E DV | mw | Tw_out | Ppump | E total
1 | 4 | 0.55 | 17 | 18 | 0.3 | 1.7218 | 1.1621 | 660 | 1540 | 5185.4 | 0.00030545 | 15.5 | 0.0072512 | 8.572 | 0.0069458 | 0.0051008 | 13756.8376 | 1650 | 10239.6008 | 0.039286 | 19 | 1.927 | 10241.5277
2 | 6 | 0.36667 | 17 | 18 | 0.35 | 1.6456 | 1.2554 | 770 | 1430 | 3666.3 | 0.00045818 | 15.5 | 0.0071581 | 8.001 | 0.0066999 | 0.0034907 | 9784.1285 | 1100 | 7201.9433 | 0.045833 | 19 | 2.2481 | 7204.1914
3 | 8 | 0.275 | 16 | 19 | 0.475 | 1.5801 | 1.4608 | 1045 | 1155 | 3769.975 | 0.00061091 | 14.5 | 0.0061377 | 5.291 | 0.0055268 | 0.0029406 | 8165.1995 | 825 | 6151.6915 | 0.1244 | 17 | 6.1021 | 6157.7936
4 | 10 | 0.22 | 16 | 19 | 0.525 | 1.5039 | 1.5542 | 1155 | 1045 | 3149.96 | 0.00076364 | 14.5 | 0.0060598 | 4.682 | 0.0052962 | 0.0024032 | 6787.2541 | 660 | 5093.1139 | 0.1375 | 17 | 6.7444 | 5099.8582
5 | 12 | 0.18333 | 15.5 | 20.5 | 0.575 | 1.4702 | 1.7035 | 1265 | 935 | 3415.3167 | 0.00091636 | 14 | 0.0052517 | 1.871 | 0.0043353 | 0.0021789 | 6234.5844 | 550 | 4794.3467 | 0.30119 | 16 | 14.7734 | 4809.1201
6 | 14 | 0.15714 | 15.5 | 20.5 | 0.6 | 1.3961 | 1.8022 | 1320 | 880 | 3041.9714 | 0.0010691 | 14 | 0.0051823 | 1.142 | 0.0041132 | 0.0019025 | 5537.1368 | 471.4286 | 4243.8475 | 0.31429 | 16 | 15.4157 | 4259.2632
c- Finding the new humidity ratio due to the water vapor generated from occupants (Wv (kg water/kg dry air)).
Np at peak load is 12
|  |  |  | wp= | 1.4e-05
d- Finding the maximum allowable humidity ratio of air near the ceiling to avoid condensation at the dew point temperature (WR (kg water/kg dry air)).
e- Finding the maximum allowed supply air humidity ratio (WS (kg water/kg dry air)) based on the new humidity ratio, maximum allowable humidity ratio of air near the ceiling and the supply one.
f- Using the balance for water, the mass of water condensate can be determined:
g- Finding the cooling coil load from the overall energy balance of the DV system:
h- Finding the fan power using the following equation:
i. Finding the DV total energy as converted to electrical equivalent as follows:
j- Finding the pump mass flow rate (kg/s) from the equation of chilled ceiling heat removal (Qcc in W):
| mw | qcc/(cpw*(Twout-Twin))
k- Finding the temperature of water exiting the chilled ceiling (Tw,out in °C) from the following equation:
Tw,in
Tw,out
l- Finding the input power of the pump Ppump (in W) as follows:
Where Hp is the pump head and is equivalent to 4 m, and ηp is the pump efficiency and is
equal to 0.8.
from the calculated figures in the table above, I would select the following three feasible R and P:
| P |  | Tc | Ts | R | H | dT/dZ
| 8 | 0.275 | 16 | 19 | 0.5 | 1.578 | 1.4555
10
12
note that all the three selections satisfy the thermal comfort and stratification height constraints. Out of the three selections, I will select the first one for P = 8 and R = 0.5 as the last has the minimum energy consumption.
| P |  | Tc | Ts | R | H | dT/dZ | Qcc | Qsdv | Qrh | Wv | Tdp,min | HR (wa, max) |  | Ws. Max | m cond | Qc | fan power P (W) | E(w) | mw | Twout | Ppump
| 8 | 0.275 | 16 | 19 | 0.5 | 1.578 | 1.4555 | 1100 | 1100 |  | 0.00061091 | 14.5 | 0.026016 |  | 0.37662 | 0.047097 |  |  | 0
T out should be higher than T in
so here we are getting T in (in cell T45)
and we fixed T out at 18
Since Tc = (Tin+Tout )/2, and we have Tout=18 and Tin < Tout indeed --> so TC is lower than 18 (between T in and T out)
and m_W = Q/cp(Tout-Tin)=Q/cp(18-Tin)
𝑚_𝑆 𝑐_𝑝𝑎 (𝑇_𝑆−𝑇_𝑅)+𝑄_𝑆−𝑄_𝐶𝐶=0
Note on U47: Elvire Katramiz (Student): here we consider T out 18
Note on AB47: Elvire Katramiz (Student): here we consider T out 18

## Load Data
Energy Conservation Assignment
1- Find the peak total sensible load per floor area (W/m2) due to equipment and at peak occupancy.
| area of room (m2) |  | 25 |  | height of room (m) |  | 3 |  | load per person (w) |  | 100 |  | load due to equipment and lighting (w) | 1000
| Hour | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Number of people | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 5 | 10 | 10 | 12
| load due to people ( w/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 16 | 20 | 40 | 40 | 48
| load due to equipment and lighting (w/m2) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
| total laod ( w/m2) | 40 | 40 | 40 | 40 | 40 | 40 | 44 | 56 | 60 | 80 | 80 | 88
| Hour | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| Number of people | 12 | 10 | 10 | 10 | 8 | 7 | 7 | 6 | 4 | 2 | 0 | 0
| load due to people ( w/m2) | 48 | 40 | 40 | 40 | 32 | 28 | 28 | 24 | 16 | 8 | 0 | 0
| load due to equipment and lighting (w/m2) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
| total laod ( w/m2) | 88 | 80 | 80 | 80 | 72 | 68 | 68 | 64 | 56 | 48 | 40 | 40
| based on the calculation above, the peak total sensible load per floor area (W/m2) due to equipment and at peak occupancy is occuring at 12 pm and 1 pm and it is equal to : | 21: 88

## Economic Analysis
Column1 | Investment | Installation | Energy | Annual Mantinance | Salvage Value | Previous Energy | liter of diesel |  |  |  | System | Initial Investment | Installation Cost | Annual Energy Cost | Salvage Value | Annual Maintenance Costs
CCDV | 1900 | 200 | 840 | 10 | 54 | 2000 | 336 |  |  |  | CC-DV | 1000$+900$ | 100$+100$ | 0.84 MWh | 54$ | 10$
Mixed-Mode | 1080 | 54 | 1500 | 10.8 | 50 | 2000 | 600 |  |  |  | Mixed Mode | 1080$ | 54$ | 1.5 MWh | 50$ | 10.8$
rate of electricity price increase | 0.02
i | 0.0475
f | 0.038
r | 0.0091522
Costs without interest rate:($)
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
CCDV | -2100 | 184.88 | 188.7776 | 192.7532 | 196.8082 | 200.9444 | 205.1633 | 209.4665 | 213.8559 | 218.333 | 222.8996 | 227.5576 | 232.3088 | 237.155 | 242.0981 | 247.14 | 252.2828 | 257.5285 | 262.879 | 268.3366 | 327.9034
Mixed Mode | -1134 | 73.2 | 74.88 | 76.5936 | 78.3415 | 80.1243 | 81.9428 | 83.7976 | 85.6896 | 87.6194 | 89.5878 | 91.5955 | 93.6434 | 95.7323 | 97.863 | 100.0362 | 102.2529 | 104.514 | 106.8203 | 109.1727 | 161.5721
Costs with intest rate:($)
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
CCDV | -2100 | 183.2033 | 185.369 | 187.5562 | 189.7652 | 191.9961 | 194.2493 | 196.525 | 198.8235 | 201.145 | 203.4898 | 205.8581 | 208.2502 | 210.6665 | 213.107 | 215.5723 | 218.0624 | 220.5778 | 223.1186 | 225.6852 | 273.2828
Mixed Mode | -1134 | 72.5361 | 73.528 | 74.5285 | 75.5379 | 76.5563 | 77.5837 | 78.6204 | 79.6663 | 80.7217 | 81.7866 | 82.8611 | 83.9455 | 85.0397 | 86.144 | 87.2584 | 88.383 | 89.5181 | 90.6637 | 91.82 | 134.6582
System | NPV($) | IRR | CER
CCDV | 2046.3034 | 8.152% | 0.97443
Mixed Mode | 557.3571 | 4.831% | 0.4915
Benefits without interest rate: ($)
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
CCDV | 0 | 336 | 342.72 | 349.5744 | 356.5659 | 363.6972 | 370.9711 | 378.3906 | 385.9584 | 393.6776 | 401.5511 | 409.5821 | 417.7738 | 426.1292 | 434.6518 | 443.3449 | 452.2118 | 461.256 | 470.4811 | 479.8907 | 543.4886
Mixed Mode | 0 | 336 | 342.72 | 349.5744 | 356.5659 | 363.6972 | 370.9711 | 378.3906 | 385.9584 | 393.6776 | 401.5511 | 409.5821 | 417.7738 | 426.1292 | 434.6518 | 443.3449 | 452.2118 | 461.256 | 470.4811 | 479.8907 | 539.4886
Costs without interest rate: ($)
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
CCDV | -2100 | -151.12 | -153.9424 | -156.8212 | -159.7577 | -162.7528 | -165.8079 | -168.924 | -172.1025 | -175.3446 | -178.6515 | -182.0245 | -185.465 | -188.9743 | -192.5538 | -196.2048 | -199.9289 | -203.7275 | -207.6021 | -211.5541 | -215.5852
Mixed Mode | -1134 | -262.8 | -267.84 | -272.9808 | -278.2244 | -283.5729 | -289.0284 | -294.5929 | -300.2688 | -306.0582 | -311.9633 | -317.9866 | -324.1303 | -330.3969 | -336.7889 | -343.3086 | -349.9588 | -356.742 | -363.6608 | -370.7181 | -377.9164
Benefits with Interest rate: ($)
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
CCDV | 0 | 332.9527 | 336.5318 | 340.1493 | 343.8057 | 347.5014 | 351.2368 | 355.0124 | 358.8286 | 362.6858 | 366.5845 | 370.525 | 374.5079 | 378.5337 | 382.6027 | 386.7154 | 390.8724 | 395.074 | 399.3209 | 403.6133 | 452.9569
Mixed Mode | 0 | 332.9527 | 336.5318 | 340.1493 | 343.8057 | 347.5014 | 351.2368 | 355.0124 | 358.8286 | 362.6858 | 366.5845 | 370.525 | 374.5079 | 378.5337 | 382.6027 | 386.7154 | 390.8724 | 395.074 | 399.3209 | 403.6133 | 449.6232
Costs with interest rate: ($)
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
CCDV | -2100 | -149.7495 | -151.1628 | -152.5931 | -154.0405 | -155.5053 | -156.9875 | -158.4874 | -160.0051 | -161.5408 | -163.0947 | -164.6669 | -166.2577 | -167.8672 | -169.4956 | -171.1432 | -172.81 | -174.4963 | -176.2023 | -177.9281 | -179.6741
Mixed Mode | -1134 | -260.4166 | -263.0038 | -265.6208 | -268.2678 | -270.9451 | -273.6531 | -276.3921 | -279.1623 | -281.9641 | -284.7979 | -287.6639 | -290.5625 | -293.494 | -296.4587 | -299.4571 | -302.4894 | -305.5559 | -308.6571 | -311.7934 | -314.9649
System | NPV Benefit | NPV Costs | B/C Ratio
CCDV | 7430.0113 | -5383.708 | 1.3801
Mixed Mode | 7426.6776 | -6869.3205 | 1.0811
System | Initial Invest+Installation | Annual cost($) | Annual Energy(KWh)
Full Diesel | 0 | 1500*electricity cost | 1500
Half Diesel Half PV | 1000 | 840*electricity cost | 1680
LCOE
Cashflow costs for energy
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Full Diesel | 0 | 252 | 257.04 | 262.1808 | 267.4244 | 272.7729 | 278.2284 | 283.7929 | 289.4688 | 295.2582 | 301.1633 | 307.1866 | 313.3303 | 319.5969 | 325.9889 | 332.5086 | 339.1588 | 345.942 | 352.8608 | 359.9181 | 367.1164
Half Diesel Half PV | 1000 | 141.12 | 143.9424 | 146.8212 | 149.7577 | 152.7528 | 155.8079 | 158.924 | 162.1025 | 165.3446 | 168.6515 | 172.0245 | 175.465 | 178.9743 | 182.5538 | 186.2048 | 189.9289 | 193.7275 | 197.6021 | 201.5541 | 205.5852
NPV costs for energy
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Full Diesel | 0 | 249.7146 | 252.3988 | 255.112 | 257.8543 | 260.6261 | 263.4276 | 266.2593 | 269.1215 | 272.0143 | 274.9383 | 277.8938 | 280.881 | 283.9003 | 286.952 | 290.0366 | 293.1543 | 296.3055 | 299.4906 | 302.71 | 305.9639
Half Diesel Half PV | 1000 | 139.8402 | 141.3434 | 142.8627 | 144.3984 | 145.9506 | 147.5195 | 149.1052 | 150.708 | 152.328 | 153.9655 | 155.6205 | 157.2933 | 158.9841 | 160.6931 | 162.4205 | 164.1664 | 165.9311 | 167.7148 | 169.5176 | 171.3398
Energy
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Full Diesel | 0 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500
Half Diesel Half PV | 0 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680
Energy with interest
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Full Diesel | 0 | 1486.3962 | 1472.9157 | 1459.5576 | 1446.3205 | 1433.2035 | 1420.2055 | 1407.3254 | 1394.562 | 1381.9144 | 1369.3816 | 1356.9624 | 1344.6558 | 1332.4608 | 1320.3764 | 1308.4017 | 1296.5355 | 1284.7769 | 1273.125 | 1261.5788 | 1250.1373
Half Diesel Half PV | 0 | 1664.7637 | 1649.6656 | 1634.7045 | 1619.879 | 1605.188 | 1590.6302 | 1576.2044 | 1561.9095 | 1547.7442 | 1533.7074 | 1519.7978 | 1506.0145 | 1492.3561 | 1478.8216 | 1465.4099 | 1452.1197 | 1438.9502 | 1425.9 | 1412.9682 | 1400.1537
System | Sum Cost | Sum Energy | LCOE($/kWh)
Full Diesel | 5538.7548 | 27300.7929 | 0.20288
Half Diesel Half PV | 4101.7027 | 30576.8881 | 0.13414

## to post
Costs without interest rate:($)
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
CCDV | -2100 | 184.88 | 188.7776 | 192.7532 | 196.8082 | 200.9444 | 205.1633 | 209.4665 | 213.8559 | 218.333 | 222.8996 | 227.5576 | 232.3088 | 237.155 | 242.0981 | 247.14 | 252.2828 | 257.5285 | 262.879 | 268.3366 | 327.9034
Mixed Mode | -1134 | 73.2 | 74.88 | 76.5936 | 78.3415 | 80.1243 | 81.9428 | 83.7976 | 85.6896 | 87.6194 | 89.5878 | 91.5955 | 93.6434 | 95.7323 | 97.863 | 100.0362 | 102.2529 | 104.514 | 106.8203 | 109.1727 | 161.5721
Costs with intest rate:($)
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
CCDV | -2100 | 183.2033 | 185.369 | 187.5562 | 189.7652 | 191.9961 | 194.2493 | 196.525 | 198.8235 | 201.145 | 203.4898 | 205.8581 | 208.2502 | 210.6665 | 213.107 | 215.5723 | 218.0624 | 220.5778 | 223.1186 | 225.6852 | 273.2828
Mixed Mode | -1134 | 72.5361 | 73.528 | 74.5285 | 75.5379 | 76.5563 | 77.5837 | 78.6204 | 79.6663 | 80.7217 | 81.7866 | 82.8611 | 83.9455 | 85.0397 | 86.144 | 87.2584 | 88.383 | 89.5181 | 90.6637 | 91.82 | 134.6582
Benefits without interest rate: ($)
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
CCDV | 0 | 336 | 342.72 | 349.5744 | 356.5659 | 363.6972 | 370.9711 | 378.3906 | 385.9584 | 393.6776 | 401.5511 | 409.5821 | 417.7738 | 426.1292 | 434.6518 | 443.3449 | 452.2118 | 461.256 | 470.4811 | 479.8907 | 543.4886
Mixed Mode | 0 | 336 | 342.72 | 349.5744 | 356.5659 | 363.6972 | 370.9711 | 378.3906 | 385.9584 | 393.6776 | 401.5511 | 409.5821 | 417.7738 | 426.1292 | 434.6518 | 443.3449 | 452.2118 | 461.256 | 470.4811 | 479.8907 | 539.4886
Costs without interest rate: ($)
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
CCDV | -2100 | -151.12 | -153.9424 | -156.8212 | -159.7577 | -162.7528 | -165.8079 | -168.924 | -172.1025 | -175.3446 | -178.6515 | -182.0245 | -185.465 | -188.9743 | -192.5538 | -196.2048 | -199.9289 | -203.7275 | -207.6021 | -211.5541 | -215.5852
Mixed Mode | -1134 | -262.8 | -267.84 | -272.9808 | -278.2244 | -283.5729 | -289.0284 | -294.5929 | -300.2688 | -306.0582 | -311.9633 | -317.9866 | -324.1303 | -330.3969 | -336.7889 | -343.3086 | -349.9588 | -356.742 | -363.6608 | -370.7181 | -377.9164
Benefits with Interest rate: ($)
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
CCDV | 0 | 332.9527 | 336.5318 | 340.1493 | 343.8057 | 347.5014 | 351.2368 | 355.0124 | 358.8286 | 362.6858 | 366.5845 | 370.525 | 374.5079 | 378.5337 | 382.6027 | 386.7154 | 390.8724 | 395.074 | 399.3209 | 403.6133 | 452.9569
Mixed Mode | 0 | 332.9527 | 336.5318 | 340.1493 | 343.8057 | 347.5014 | 351.2368 | 355.0124 | 358.8286 | 362.6858 | 366.5845 | 370.525 | 374.5079 | 378.5337 | 382.6027 | 386.7154 | 390.8724 | 395.074 | 399.3209 | 403.6133 | 449.6232
Costs with interest rate: ($)
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
CCDV | -2100 | -149.7495 | -151.1628 | -152.5931 | -154.0405 | -155.5053 | -156.9875 | -158.4874 | -160.0051 | -161.5408 | -163.0947 | -164.6669 | -166.2577 | -167.8672 | -169.4956 | -171.1432 | -172.81 | -174.4963 | -176.2023 | -177.9281 | -179.6741
Mixed Mode | -1134 | -260.4166 | -263.0038 | -265.6208 | -268.2678 | -270.9451 | -273.6531 | -276.3921 | -279.1623 | -281.9641 | -284.7979 | -287.6639 | -290.5625 | -293.494 | -296.4587 | -299.4571 | -302.4894 | -305.5559 | -308.6571 | -311.7934 | -314.9649
Cashflow costs for energy
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Full Diesel | 0 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252
Half Diesel Half PV | 1000 | 141.12 | 141.12 | 141.12 | 141.12 | 141.12 | 141.12 | 141.12 | 141.12 | 141.12 | 141.12 | 141.12 | 141.12 | 141.12 | 141.12 | 141.12 | 141.12 | 141.12 | 141.12 | 141.12 | 141.12
NPV costs for energy
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Full Diesel | 0 | 249.7146 | 252.3988 | 255.112 | 257.8543 | 260.6261 | 263.4276 | 266.2593 | 269.1215 | 272.0143 | 274.9383 | 277.8938 | 280.881 | 283.9003 | 286.952 | 290.0366 | 293.1543 | 296.3055 | 299.4906 | 302.71 | 305.9639
Half Diesel Half PV | 1000 | 139.8402 | 141.3434 | 142.8627 | 144.3984 | 145.9506 | 147.5195 | 149.1052 | 150.708 | 152.328 | 153.9655 | 155.6205 | 157.2933 | 158.9841 | 160.6931 | 162.4205 | 164.1664 | 165.9311 | 167.7148 | 169.5176 | 171.3398
Energy with interest
System | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Full Diesel | 0 | 1486.3962 | 1472.9157 | 1459.5576 | 1446.3205 | 1433.2035 | 1420.2055 | 1407.3254 | 1394.562 | 1381.9144 | 1369.3816 | 1356.9624 | 1344.6558 | 1332.4608 | 1320.3764 | 1308.4017 | 1296.5355 | 1284.7769 | 1273.125 | 1261.5788 | 1250.1373
Half Diesel Half PV | 0 | 1664.7637 | 1649.6656 | 1634.7045 | 1619.879 | 1605.188 | 1590.6302 | 1576.2044 | 1561.9095 | 1547.7442 | 1533.7074 | 1519.7978 | 1506.0145 | 1492.3561 | 1478.8216 | 1465.4099 | 1452.1197 | 1438.9502 | 1425.9 | 1412.9682 | 1400.1537