## Slide 1
American University of Beirut
MECH 674
Energy Economics and Policy
Dr. Carine Habchi
Project : CCDV vs Mixed-mode Ventilation Economic Analysis
Prepared by:
Ahmad El Haj
Jihad Jundi
Mohammad El Masri

## Slide 2: Problem
The office space dimensions are 5 m x 5 m x 3 m.
The internal load due to equipment and lighting is fixed at 1000 W.
The internal load per person is 100 W
Maximum Occupancy in the office space is 12 persons.
The office is located close to available seawater at a temperature of .

## Slide 3: Problem
The occupancy and weather conditions are given per hour of the day.
After calculation, we find the maximum load to be 88 W/
What should we use to solve our problem?

## Slide 4: Different options?
Option 1: Mixed-mode ventilation system using mechanical systems like windows and refrigeration systems in order to provide adjustable ventilation.
  Information was taken from a previous study done on a bigger office building.
  This will be powered purely by a diesel generator.
Option 2: CC-DV system which we will design and size accordingly.
  We will use seawater in order to cool our chilled ceiling.
  A fan of efficiency 0.5 and a pressure difference of 1.5 kPa will be used in order to supply air in the DV system.
  A pump of efficiency 0.8 and a pump head of 4 m will be used in order to circulate seawater to the chilled ceiling.
  This will be powered 50% by a diesel generator and 50% by PV panels.

## Slide 5
Our objective is to make several designs of
Chilled ceiling and displacement ventilation
System to make sure that the thermal comfort
(dT/dz ) and the air quality (H>1m)
standards are met. We wanted to make sure that
avoid condensate forming on the chilled
ceiling.
System Description:
Office space dimension: 5 m x 5 m x 3 m
The internal load due to equipment and lighting is
fixed at 1000 W.
The internal load per person is 100 W
Maximum Occupancy in the office space is 12 persons.
The seawater used to cool the chilled ceiling comes
in at a temperature of .
The fan efficiency is 0.5 and the pressure difference
is 1.5 kPa.
The pump efficiency is 0.8 and the pump head is
equivalent to 4 m.

## Slide 6
The load due to equipment per unit area is calculated as follows:
The load due to people is calculated as follows:
the maximum load is and is equal to

## Slide 7
Design | P | mdot | Tc | Ts | R | H | dT/dZ
1 | 4 | 0.55 | 17 | 18 | 0.3 | 1.7218 | 1.1621
2 | 6 | 0.37 | 17 | 18 | 0.35 | 1.6456 | 1.25545
3 | 8 | 0.28 | 16 | 19 | 0.475 | 1.5801 | 1.460825
4 | 10 | 0.22 | 16 | 19 | 0.525 | 1.5039 | 1.554175
5 | 12 | 0.18 | 15.5 | 20.5 | 0.575 | 1.4702 | 1.703525
6 | 14 | 0.16 | 15.5 | 20.5 | 0.6 | 1.3961 | 1.8022
The supplied mass flow rate can be calculated using the below formula:

## Slide 8
The exhaust temperature can be calculated using the below formula:
Where Hr is the height of the room=3m
Design | P | mdot | Ts | dT/dZ | Tr
1 | 4 | 0.55 | 18 | 1.1621 | 20.61473
2 | 6 | 0.37 | 18 | 1.25545 | 20.82476
3 | 8 | 0.28 | 19 | 1.460825 | 22.28686
4 | 10 | 0.22 | 19 | 1.554175 | 22.49689
5 | 12 | 0.18 | 20.5 | 1.703525 | 24.33293
6 | 14 | 0.16 | 20.5 | 1.8022 | 24.55495

## Slide 9
The energy removed by the ceiling and that removed by the displacement ventilation are added up sensible load generated in the room. They can be determined by the following relations:
-
Design | R | Qs | Qcc | Qsdv
1 | 0.3 | 88 | 660 | 1540
2 | 0.35 | 88 | 770 | 1430
3 | 0.475 | 88 | 1045 | 1155
4 | 0.525 | 88 | 1155 | 1045
5 | 0.575 | 88 | 1265 | 935
6 | 0.6 | 88 | 1320 | 880

## Slide 10
The humidity ratio due to water vapor generated by the occupants is given by:
Where is the water vapor rate generated by each person equals to
Design | mdot | Wv
1 | 0.55 | 0.000305
2 | 0.37 | 0.000458
3 | 0.28 | 0.000611
4 | 0.22 | 0.000764
5 | 0.18 | 0.000916
6 | 0.16 | 0.001069

## Slide 11
The maximum allowable humidity ratio of air near the ceiling to avoid condensation at the dew point temperature.
Where the dew point temperature of the ceiling is
Design | Tc | Tdp,min | Tr | HR (wa, max)
1 | 17 | 15.5 | 20.61473 | 0.007251
2 | 17 | 15.5 | 20.82476 | 0.007158
3 | 16 | 14.5 | 22.28686 | 0.006138
4 | 16 | 14.5 | 22.49689 | 0.00606
5 | 15.5 | 14 | 24.33293 | 0.005252
6 | 15.5 | 14 | 24.55495 | 0.005182

## Slide 12
the maximum allowed supply air humidity ratio ( is given by:
Thus, we can calculate the reheat energy from to based on the following equation:
Where the dew point temperature can be founded based on the supply humidity ratio and relative humidity 100% through the psychometric chart.
Design | HR (wa, max) | Wv | Ws. Max | Tdp | Qrh
1 | 0.007251 | 0.000305 | 0.006946 | 8.572 | 5185.4
2 | 0.007158 | 0.000458 | 0.0067 | 8.001 | 3666.3
3 | 0.006138 | 0.000611 | 0.005527 | 5.291 | 3769.975
4 | 0.00606 | 0.000764 | 0.005296 | 4.682 | 3149.96
5 | 0.005252 | 0.000916 | 0.004335 | 1.871 | 3415.317
6 | 0.005182 | 0.001069 | 0.004113 | 1.142 | 3041.971

## Slide 13
The mass of water condensate can be calculated by applying mass balance for water:
Where:
is he highest ambient humidity at peak load is
is wa, max
=
Design | mFA | HR (wa, max) | Wv | mdot | m cond
1 | 0.55 | 0.007251 | 0.000305 | 0.55 | 0.005101
2 | 0.37 | 0.007158 | 0.000458 | 0.37 | 0.003491
3 | 0.28 | 0.006138 | 0.000611 | 0.28 | 0.002941
4 | 0.22 | 0.00606 | 0.000764 | 0.22 | 0.002403
5 | 0.18 | 0.005252 | 0.000916 | 0.18 | 0.002179
6 | 0.16 | 0.005182 | 0.001069 | 0.16 | 0.001902

## Slide 14
The cooling coil load can be determined using the following equation by applying energy balance on the entire DV system:
Design | Qrh | m cond | hfg | mdot | Cpa | Ts | Qc (w)
1 | 5185.4 | 0.005101 | 2257 | 0.55 | 1005 | 18 | 13756.84
2 | 3666.3 | 0.003491 | 2257 | 0.37 | 1005 | 18 | 9784.129
3 | 3769.975 | 0.002941 | 2257 | 0.28 | 1005 | 19 | 8165.2
4 | 3149.96 | 0.002403 | 2257 | 0.22 | 1005 | 19 | 6787.254
5 | 3415.317 | 0.002179 | 2257 | 0.18 | 1005 | 20.5 | 6234.584
6 | 3041.971 | 0.001902 | 2257 | 0.16 | 1005 | 20.5 | 5537.137

## Slide 15
Fan Power
The fan efficiency is 0.5 and the pressure difference is 1.5 kPa.
The density of air is taken to be equal 1 kg/m^3
Electrical Total; energy of DV system:
Design | mdot | fan power P (W) | E DV
1 | 0.55 | 1,650.00 | 10,239.60
2 | 0.37 | 1,100.00 | 7,201.94
3 | 0.28 | 825 | 6,151.69
4 | 0.22 | 660 | 5,093.11
5 | 0.18 | 550 | 4,794.35
6 | 0.16 | 471.43 | 4,243.85

## Slide 16
Chilled ceiling water exiting temperature Tw,out:
Pump’s mass flow rate :
Pump Power:
Total System Electrical Energy:
Design | mw | Tw_out | Ppump | E total
1 | 0.039286 | 19 | 1.926964 | 10,241.53
2 | 0.045833 | 19 | 2.248125 | 7,204.19
3 | 0.124405 | 17 | 6.102054 | 6,157.79
4 | 0.1375 | 17 | 6.744375 | 5,099.86
5 | 0.30119 | 16 | 14.77339 | 4,809.12
6 | 0.314286 | 16 | 15.41571 | 4,259.26

## Slide 17
Relative Humidity Ratio Calculation:
Designs | Tr (degrees Celsius) | Specific Humidity (HR) (Kg of H2O/Kg of air | Relative Humidity (%)
1 | 20.61473 | 0.007251224 | 47%
2 | 20.82476 | 0.007158051 | 45%
3 | 22.28686 | 0.006137678 | 40%
4 | 22.49689 | 0.006059797 | 38%
5 | 24.33293 | 0.005251669 | 35%
6 | 24.55495 | 0.005182324 | 31%

## Slide 18
Recommendation:
All the stratification height and the vertical temperature values satisfy the requirements
All six designs have also been adjusted to avoid condensation on the chilled ceiling with a factor of safety of . Thus, no condensation will occur.
The CO2 concentration does not go above 1000 ppm . This implies that the Displacement Ventilation system is providing enough air at the respective flow rates for each design.
We consider the optimum range of thermal comfort to be at an optimum room temperature of with an acceptable range of
In addition, designs 1 and 2 room temperatures are outside the desired range and might cause thermal discofmort.
 Designs 1 and 2 are not acceptable.
The relative humidity values are in the thermal comfort range 30%-70%. But designs 5 and 6 have low value that might cause dryness.

## Slide 19
 | Tr | RH | Etot
Design 3 | 22.28685625 | 40 | 6,157.79
Design 4 | 22.49689375 | 38 | 5,099.86
Design 5 | 24.33293125 | 35 | 4,809.12
Design 6 | 24.55495 | 31 | 4,259.26
The table above shows that design 6 is the most energy efficient design.

## Slide 20: Simulation
The occupants were represented by 12 cylinders with height 1.1m distributed evenly in the room with the following mesh.
The meshing of both systems is done in a manner to obtain around 150000 elements with an average orthogonality of 0.76 and a maximum skewness of 0.8. Inflation is applied in the space surrounding the occupants to allow for better resolution since this volume is the most important

## Slide 21: Simulation
The CCDV system had 2 inlets at the base of the wall and the outlet in the ceiling.

## Slide 22: Simulation
The Mixed ventilation system had 2 inlets and 1 outlet in the ceiling.

## Slide 23: Simulation Conditions
We imposed a 0.16kg/s flow rate of air at the inlets of both systems
The temperature of the inlet flow for both systems is taken as that of the ambient 20.5C for CCDV as indicated in the design
The CCDV system has a ceiling temperature of 15.5C

## Slide 24: Simulation Results
From the simulation, the temperature head and chest zones of the occupants in the mixed ventilation is around 30C while in the case of CCDV system, it is 25C.
The simulations are illustrated as follows in contour and vector forms.
According to ASHRAE, thermal comfort is attained mainly in the head and chest zones. That is why we are seeing the temperature in those zones are below the temperatures at the feet.

## Slide 25: CCDV Results

## Slide 26: Mixed Ventilation Results

## Slide 27: Economic Analysis
A study Period of 20 years will be taken, and the expenses are as shown.
The electricity price is assumed equal to 0.168$/KWh with an annual increase in 2%.
The electricity is assumed to be provided by a diesel power plant, which has a fuel-to-energy ratio of . So, 336 Liters of diesel are needed for the CC-DV system and 600 Liters for the Mixed Mode system.
The annual nominal interest rate is 4.75% and the annual inflation rate is 3.8%. Therefore, the annual real interest rate is 0.915%.
We will assume that before this project, the owners were using 2 MWh per year for air conditioning and ventilation using split units.

## Slide 28: Cash Flows

## Slide 29: NPV and CER

## Slide 30: Internal Rate of Return

## Slide 31: Results
System | NPV($) | IRR | CER
CCDV | 2046.30 | 8% | 0.974430167
Mixed Mode | 557.36 | 5% | 0.491496583
 CCDV better using these 2 parameters

## Slide 32: Benefit-Cost Analysis

## Slide 33: Benefits and costs without interest

## Slide 34: NPV of Benefits and Costs

## Slide 35: Benefit-Cost Ratio (B/C)
System | NPV Benefit | NPV Costs | B/C Ratio
CCDV | 7430.01 | -5383.71 | 1.380091819
Mixed Mode | 7426.68 | -6869.32 | 1.081137156
>
 CCDV is better based on Benefit-Cost Analysis

## Slide 36: Electricity Generation Analysis
System | Initial Invest +Installation | Annual Energy cost($) | Annual Energy Production(kWh)
Full Diesel | 0 | 1500*electricity cost | 1500
Half Diesel Half PV | 1000 | 840*electricity cost | 1680

## Slide 37: Energy Cost Cash Flows and NPV

## Slide 38: Energy produced including interest

## Slide 39: Levelised Cost of Electricity
System | Sum Cost | Sum Energy | LCOE($/kWh)
Full Diesel | 5538.754778 | 27300.79291 | 0.202878898
Half Diesel Half PV | 4101.702676 | 30576.88806 | 0.134143889
 Encouraging the use of the CCDV system based on cost of electricity.

## Slide 40: Final Decision
All methods of analysis either CER, IRR, benefit-cost, or electricity cost indicate that the better HVAC system to be used is the CCDV system in this problem.
CCDV > Mixed-Mode

## Slide 41
Thank you