## 2
Using the design chart of CC/DV system based on the calculated peak sensible load per floor area ( 80-90 w/m2) and different values of P (flow rate parameter) below, we find the different parameters (chilled ceiling temperature (°C), supply air temperature (°C), load removal ratio, stratification height (m) and temperature gradient (°C/m)).
|  | room area |  |  | A | 25
|  | the peak total sensible load per floor area (W/m2) |  |  | Qs | 88
|  | chilled ceiling temperature (°C) |  |  | Tc | 16
|  | supply air temperature (°C) |  |  | Ts | 19
|  | load removal ratio |  |  | R | 0.5
|  | stratification height (m) |  |  | H | 1.578
|  | temperature gradient (°C/m) |  |  | dT/dZ | 1.4608
|  | peak sensible load (w/m2) |  |  | Qs | 88
|  | ratio of cooling load to supply mass flow rate P=Qs/m˙s ( kJ/kg) |  |  | P | 8
The following equations are used to assess if the proposed system satisfies thermal comfort and indoor air quality requirements.
|  | P | mdot | Tc | Ts | R | H | dT/dZ
|  | 4 | 0.55 | 17 | 18 | 0.3 | 1.7218 | 1.1621
|  | 6 | 0.36667 | 17 | 18 | 0.35 | 1.6456 | 1.2554
|  | 8 | 0.275 | 16 | 19 | 0.475 | 1.5801 | 1.4608
|  | 10 | 0.22 | 16 | 19 | 0.525 | 1.5039 | 1.5542
|  | 12 | 0.18333 | 15.5 | 20.5 | 0.575 | 1.4702 | 1.7035
|  | 14 | 0.15714 | 15.5 | 20.5 | 0.6 | 1.3961 | 1.8022
After satisfying the requirements of comfort ( H> 1m) and indoor air quality (dT/dZ<2.5 oC/m), the energy consumption of the DV and CC system can be found by doing the following:
a. Finding the exhaust air temperature Tr (°C) as follows:
Design | P | mdot | Ts | dT/dZ | Tr
1 | 4 | 0.55 | 18 | 1.1621 | 20.6147
2 | 6 | 0.36667 | 18 | 1.2554 | 20.8248
3 | 8 | 0.275 | 19 | 1.4608 | 22.2869
4 | 10 | 0.22 | 19 | 1.5542 | 22.4969
5 | 12 | 0.18333 | 20.5 | 1.7035 | 24.3329
6 | 14 | 0.15714 | 20.5 | 1.8022 | 24.5549
b- Finding the amount of reheat used from the following energy balance:
1000
Design | P | mdot | Tc | Ts | R | H | dT/dZ | Qcc | Qsdv | Qrh | Wv | Tdp,min | HR (wa, max) | Tdp | Ws. Max | m cond | Qc | fan power P (W) | E DV | mw | Tw_out | Ppump | E total
1 | 4 | 0.55 | 17 | 18 | 0.3 | 1.7218 | 1.1621 | 660 | 1540 | 5185.4 | 0.00030545 | 15.5 | 0.0072512 | 8.572 | 0.0069458 | 0.0051008 | 13756.8376 | 1650 | 10239.6008 | 0.039286 | 19 | 1.927 | 10241.5277
2 | 6 | 0.36667 | 17 | 18 | 0.35 | 1.6456 | 1.2554 | 770 | 1430 | 3666.3 | 0.00045818 | 15.5 | 0.0071581 | 8.001 | 0.0066999 | 0.0034907 | 9784.1285 | 1100 | 7201.9433 | 0.045833 | 19 | 2.2481 | 7204.1914
3 | 8 | 0.275 | 16 | 19 | 0.475 | 1.5801 | 1.4608 | 1045 | 1155 | 3769.975 | 0.00061091 | 14.5 | 0.0061377 | 5.291 | 0.0055268 | 0.0029406 | 8165.1995 | 825 | 6151.6915 | 0.1244 | 17 | 6.1021 | 6157.7936
4 | 10 | 0.22 | 16 | 19 | 0.525 | 1.5039 | 1.5542 | 1155 | 1045 | 3149.96 | 0.00076364 | 14.5 | 0.0060598 | 4.682 | 0.0052962 | 0.0024032 | 6787.2541 | 660 | 5093.1139 | 0.1375 | 17 | 6.7444 | 5099.8582
5 | 12 | 0.18333 | 15.5 | 20.5 | 0.575 | 1.4702 | 1.7035 | 1265 | 935 | 3415.3167 | 0.00091636 | 14 | 0.0052517 | 1.871 | 0.0043353 | 0.0021789 | 6234.5844 | 550 | 4794.3467 | 0.30119 | 16 | 14.7734 | 4809.1201
6 | 14 | 0.15714 | 15.5 | 20.5 | 0.6 | 1.3961 | 1.8022 | 1320 | 880 | 3041.9714 | 0.0010691 | 14 | 0.0051823 | 1.142 | 0.0041132 | 0.0019025 | 5537.1368 | 471.4286 | 4243.8475 | 0.31429 | 16 | 15.4157 | 4259.2632
c- Finding the new humidity ratio due to the water vapor generated from occupants (Wv (kg water/kg dry air)).
Np at peak load is 12
|  |  |  | wp= | 1.4e-05
d- Finding the maximum allowable humidity ratio of air near the ceiling to avoid condensation at the dew point temperature (WR (kg water/kg dry air)).
e- Finding the maximum allowed supply air humidity ratio (WS (kg water/kg dry air)) based on the new humidity ratio, maximum allowable humidity ratio of air near the ceiling and the supply one.
f- Using the balance for water, the mass of water condensate can be determined:
g- Finding the cooling coil load from the overall energy balance of the DV system:
h- Finding the fan power using the following equation:
i. Finding the DV total energy as converted to electrical equivalent as follows:
j- Finding the pump mass flow rate (kg/s) from the equation of chilled ceiling heat removal (Qcc in W):
| mw | qcc/(cpw*(Twout-Twin))
k- Finding the temperature of water exiting the chilled ceiling (Tw,out in °C) from the following equation:
Tw,in
Tw,out
l- Finding the input power of the pump Ppump (in W) as follows:
Where Hp is the pump head and is equivalent to 4 m, and ηp is the pump efficiency and is
equal to 0.8.
from the calculated figures in the table above, I would select the following three feasible R and P:
| P |  | Tc | Ts | R | H | dT/dZ
| 8 | 0.275 | 16 | 19 | 0.5 | 1.578 | 1.4555
10
12
note that all the three selections satisfy the thermal comfort and stratification height constraints. Out of the three selections, I will select the first one for P = 8 and R = 0.5 as the last has the minimum energy consumption.
| P |  | Tc | Ts | R | H | dT/dZ | Qcc | Qsdv | Qrh | Wv | Tdp,min | HR (wa, max) |  | Ws. Max | m cond | Qc | fan power P (W) | E(w) | mw | Twout | Ppump
| 8 | 0.275 | 16 | 19 | 0.5 | 1.578 | 1.4555 | 1100 | 1100 |  | 0.00061091 | 14.5 | 0.026016 |  | 0.37662 | 0.047097 |  |  | 0
T out should be higher than T in
so here we are getting T in (in cell T45)
and we fixed T out at 18
Since Tc = (Tin+Tout )/2, and we have Tout=18 and Tin < Tout indeed --> so TC is lower than 18 (between T in and T out)
and m_W = Q/cp(Tout-Tin)=Q/cp(18-Tin)
𝑚_𝑆 𝑐_𝑝𝑎 (𝑇_𝑆−𝑇_𝑅)+𝑄_𝑆−𝑄_𝐶𝐶=0
Note on U47: Elvire Katramiz (Student): here we consider T out 18
Note on AB47: Elvire Katramiz (Student): here we consider T out 18

## 1
Energy Conservation Assignment
1- Find the peak total sensible load per floor area (W/m2) due to equipment and at peak occupancy.
| area of room (m2) |  | 25 |  | height of room (m) |  | 3 |  | load per person (w) |  | 100 |  | load due to equipment and lighting (w) | 1000
| Hour | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Number of people | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 5 | 10 | 10 | 12
| load due to people ( w/m2) | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 16 | 20 | 40 | 40 | 48
| load due to equipment and lighting (w/m2) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
| total laod ( w/m2) | 40 | 40 | 40 | 40 | 40 | 40 | 44 | 56 | 60 | 80 | 80 | 88
| Hour | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| Number of people | 12 | 10 | 10 | 10 | 8 | 7 | 7 | 6 | 4 | 2 | 0 | 0
| load due to people ( w/m2) | 48 | 40 | 40 | 40 | 32 | 28 | 28 | 24 | 16 | 8 | 0 | 0
| load due to equipment and lighting (w/m2) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
| total laod ( w/m2) | 88 | 80 | 80 | 80 | 72 | 68 | 68 | 64 | 56 | 48 | 40 | 40
| based on the calculation above, the peak total sensible load per floor area (W/m2) due to equipment and at peak occupancy is occuring at 12 pm and 1 pm and it is equal to : | 21: 88

## Sheet1
|  |  |  | Designs | Tr (degrees Celsius) | Specific Humidity (HR) (Kg of H2O/Kg of air | Relative Humidity (%)
| Tr | RH | Etot | 1 | 20.6147 | 0.0072512 | 47%
Design 3 | 22.2869 | 40 | 6157.7936 | 2 | 20.8248 | 0.0071581 | 45%
Design 4 | 22.4969 | 38 | 5099.8582 | 3 | 22.2869 | 0.0061377 | 40%
Design 5 | 24.3329 | 35 | 4809.1201 | 4 | 22.4969 | 0.0060598 | 38%
Design 6 | 24.5549 | 31 | 4259.2632 | 5 | 24.3329 | 0.0052517 | 35%
|  |  |  | 6 | 24.555 | 0.0051823 | 31%